WATERLINE NOTES

- WCWD POSSESSES THE AUTHORITY TO IMPLEMENT FIELD ADJUSTMENTS AS DEEMED NECESSARY, EVEN IF SUCH MODIFICATIONS DEVIATE FROM THE APPROVED PLANS.

- WATERLINES SHOULD BE THE LAST UTILITY INSTALLED UNLESS AUTHORIZED BY WCWD.

- BEFORE ANY INSTALLATION OF WATERLINES, FINAL GRADING MUST BE COMPLETED.

- NO PROPOSED UTILITIES SHALL BE INSTALLED WITHIN 5 FEET ON EITHER SIDE OF THE PROPOSED WATERLINES.

- WATERLINES SHALL HAVE A MINIMUM COVER OF 30 INCHES. ANY WATERLINES 12 INCHES IN DIAMETER OR LARGER SHALL HAVE A MINIMUM COVER OF 48 INCHES.

- ALL WATERLINES SHALL BE DR18 C900 OR DIP WHERE REQUIRED.

- ALL BEDDING AND BACKFILL SHALL BE IN ACCORDANCE WITH WCWD STANDARD SPECIFICATIONS AND 10 STATES STANDARDS.

- INSTALL MECHNICAL JOINT BENDS AS REQUIRED TO LIMIT RADIUS OF WATERLINE CURVATURE TO MANUFACTURER'S REQUIREMENTS OR AS REQUIRED BY WCWD.

- GATE VALVES AT TEES SHALL BE RESTRAINED BY FOSTER ADAPTER OR SOLID SWIVEL.

- ALL CONNECTIONS TO EXISTING WATERLINES SHALL BE PERFORMED BY WCWD APPROVED CONTRACTOR IN ACCORDANCE WITH THE WATERLINE EXTENSION AGREEMENT AT THE CONTRACTOR’S EXPENSE. MATERIALS SHALL BE FURNISHED BY THE CONTRACTOR.

- FOR ANY UTILITY CROSSING BETWEEN WATER, SEWER, FORCEMAIN, AND STORM SEWER WITH A VERTICAL SEPARATION OF LESS THAN 18 INCHES, REFERENCE WCWD TYPICAL UTLITY CROSSING DETAIL. WCWD WILL NOT APPROVE UTILITY CROSSINGS THAT HAVE LESS THAN 6 INCHES OF VERTICAL SEPARATION.

- IN AREAS WHERE 1” OR SMALLER SERVICE LINES ARE PROPOSED UNDER SIDEWALKS, DRIVEWAYS, OR PAVEMENT, 2” SCHEDULE 40 PVC CASINGS SHALL BE INSTALLED FOR THE SERVICE LINE.

- FIRE PROTECTION LINES SHALL BE DISINFECTED, TESTED, AND ACCEPTED IN ACCORDANCE WITH WCWD STANDARD SPECIFICATIONS BEFORE BEING PLACED IN SERVICE.

- ALL SERVICE LINES ENDING IN VALVES FOR LARGE METERS SHALL BE RESTRAINED TO THE TEE IN LEIU OF THE INSTALLATION OF A REVERSE CONCRETE ANCHOR (DEADMAN).

- METER INSTALLATIONS ARE TO BE PERFORMED BY WCWD.

- NO TREE PLANTINGS SHALL BE PROPOSED WITHIN 5 FEET OF ANY PROPOSED WATERLINES.

- THE PROPOSED PROJECT HAS XXX ZONING, XXX LINEAR FEET OF PROPOSED WATER MAIN, AND XXX WATER METER INSTALLATIONS.

SANITARY SEWER NOTES

- WCWD POSSESSES THE AUTHORITY TO IMPLEMENT FIELD ADJUSTMENTS AS DEEMED NECESSARY, EVEN IF SUCH MODIFICATIONS DEVIATE FROM THE APPROVED PLANS.

- BEFORE ANY INSTALLATION OF SEWER LINES, FINAL GRADING MUST BE COMPLETED.

- NO PROPOSED UTILITIES SHALL BE INSTALLED WITHIN 10 FEET ON EITHER SIDE OF THE PROPOSED SEWER LINES.

- SANITARY SEWER SHALL HAVE A MINIMUM COVER OF 48 INCHES.

- ALL SEWER LINES SHALL BE SDR-35 OR PS-46 UP TO A DEPTH OF 20 FEET. AT DEPTHS GREATER THAN 20 FEET, USE SDR-26 OR PS-115.

- ALL BEDDING AND BACKFILL SHALL BE IN ACCORDANCE WITH WCWD STANDARD SPECIFICATIONS AND 10 STATES STANDARDS.

- ALL CONNECTIONS TO EXISTING SEWER LINES SHALL BE PERFORMED BY WCWD APPROVED CONTRACTOR IN ACCORDANCE WITH THE SEWER LINE EXTENSION AGREEMENT AT THE CONTRACTOR’S EXPENSE. MATERIALS SHALL BE FURNISHED BY THE CONTRACTOR.

- ALL SERVICE CONNECTIONS SHALL BE 6 INCHES IN DIAMETER AND INSTALLED PER WCWD STANDARD SEWER SERVICE DETAIL UNLESS OTHERWISE APPROVED BY WCWD.

- FOR ANY UTILITY CROSSING BETWEEN WATER, SEWER, FORCEMAIN, AND STORM SEWER WITH A VERTICAL SEPARATION OF LESS THAN 18 INCHES, REFERENCE WCWD STANDARD TYPICAL UTLITY CROSSING DETAIL. WCWD WILL NOT APPROVE UTILITY CROSSINGS THAT HAVE LESS THAN 6 INCHES OF VERTICAL SEPARATION.

- THE COLLECTION SYSTEM HAS BEEN VERIFIED BY THE SIGNING ENGINEER TO BE SUFFICIENTLY DEEP TO SERVICE EACH PROPOSED STRUCTURE.

- IF STRUCTURES ARE PROPOSED TO BE INSTALLED IN DISTURBED SOIL, COORDINATE WITH WCWD FOR DESIGN TO PREVENT SETTLING ISSUES.

- A 30-DAY WAITING PERIOD IS REQUIRED AFTER THE FINAL MANHOLE IS SET TO ALLOW FOR PROPER SETTLING BEFORE TESTING CAN OCCUR. COORDINATE WITH THE WSB INSPECTOR TO SCHEDULE A TESTING DATE.

- NO TREE PLANTINGS SHALL BE PROPOSED WITHIN 5 FEET OF ANY PROPOSED SEWER LINES.

- ALL SEWER SERVICES CONNECTED TO MANHOLES SHALL BE LOW AIR TESTED AT THE MANHOLE.

- IF PROPOSING FORCEMAIN, INSTALL MECHNICAL JOINT BENDS AS REQUIRED TO LIMIT RADIUS OF FORCE MAIN CURVATURE TO MANUFACTURER'S REQUIREMENTS OR AS REQUIRED BY WCWD.

- THE PROPOSED PROJECT HAS XXX ZONING, XXX LINEAR FEET OF PROPOSED SEWER MAIN, AND XXX LINEAR FEET OF SEWER LATERAL SERVICES.